| Questionnaire Title | Facilities and Activities and Exposure Situations |
| --- | --- |
| Module Name | Regulation of Nuclear Power Plants |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | What are the provisions in place for authorization (licensing) of nuclear power plant (NPP) during the different phases of their life cycle? [Topic 5.2] | A | F |
| Expectation | [Note: This primary question is only to reveal any specific information related to authorizations as it applies to NPPs. DO NOT REPEAT information that has already been provided in the core modules dealing with GSR Part 1 (Rev. 1)]. Specific provisions are in place for authorization (licensing) of NPPs during the different stages of their life cycle. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Different types of authorization are required to be obtained for the different stages in the lifetime of a facility. The authorization process may differ among States but the main stages in the lifetime of a NPPs are: - Site evaluation; - Design; - Construction; - Commissioning; - Operation, including utilization and modification; - Decommissioning; - Release from regulatory control. |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. GSR Part 1 (Rev. 1) |  | 46 | Requirement 23 |
| Safety Standards Series No. GSG-13 | Functions and Processes of the Regulatory Body for Safety | 45 |  |
| Safety Standards Series No. SSG-12 | Licensing Process for Nuclear Installations | 25 |  |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements or guidance provided to the applicant regarding the content of the safety analysis report to be submitted with the authorization application for an NPP. [Topic 5.2] | A | F |
| Expectation | The requirements or guidance address the content of the safety analysis report including: - Detailed description of the NPP site, NPP, and all facilities and activities with safety significance; - General safety principles and criteria to be applied to the design; - Analysis of potential hazards associated with operation of the NPP; - Safety analyses of accident sequences; - Safety features to avoid or minimize likelihood of accidents or mitigate consequences; - Information for establishing the OLCs for the NPP; - Conduct of operations; - Management system program for all stages of NPP life; - Details of the emergency plan of the NPP. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Clear definition of format and content of a safety analysis report facilitates the authorization process and enhances the predictability of the regulatory body. Please also refer to safety guides SSG-61 (Format and Content of the Safety Analysis Report for Nuclear Power Plants) and SSG-70 (Operational Limits and Conditions and Operating Procedures for Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. GSR Part 1 (Rev. 1) |  | 47 | Requirement 24 |
| Safety Standards Series No. SSG-64 | Format and Content of the Safety Analysis Report for Nuclear Power Plants | 33 |  |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the provisions in place for the regulatory body to review and assess the information to be submitted by the NPP operating organizations? [Topic 6.2] | A | F |
| Expectation | [Note: This primary question is only to reveal any specific information related to review and assessment as it applies to NPPs. DO NOT REPEAT information that has already been provided in the core modules dealing with GSR Part 1 (Rev. 1) and GSR Part 4]. The regulatory body is required, and has the authority, to review and assess information provided by the operating organization in support of an application for authorization. The regulatory body regularly reviews the effectiveness of the operating organization in managing operational safety of the NPP, in implementing, applying, and reviewing and revising as necessary operational safety programmes, and in ensuring continuing safety of the plant design. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The general requirements for regulatory review and assessment are covered by the core questions dealing with GSR Part 1 and GSR Part 4. |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. GSR Part 1 (Rev. 1) |  | 49 | Requirement 25, 26 |
| Safety Standards Series No. GSG-13 | Functions and Processes of the Regulatory Body for Safety | 69 |  |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the provisions in place for a regulatory inspection programme for NPPs? [Topic 7.2] | A | F |
| Expectation | [Note: This primary question and the related subsidiary question(s) are only to reveal any specific information related to review and assessment as it applies to NPPs. DO NOT REPEAT information that has already been provided in the core modules dealing with GSR Part 1 (Rev. 1).] The regulatory inspection programme for NPPs addresses: - Inspection of facilities and activities; - Types of inspections; - Application of a graded approach to inspection activities. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The general requirements for regulatory inspection are covered by the core question sets dealing with GSR Part 1 (Rev. 1). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. GSR Part 1 (Rev. 1) |  | 51 | Requirement 27, 28, 29 |
| Safety Standards Series No. GSG-13 | Functions and Processes of the Regulatory Body for Safety | 88 |  |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What are the objectives and the scope of inspections conducted by or for the regulatory body during the construction stage of NPPs? [Topic 7.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework and/or the management system of the regulatory body specifies that the objective of the programme of inspections developed by the regulatory body regarding the construction stage of an NPP. Such inspection programme includes inspections or audits on the construction site as well as in facilities where items important to safety are manufactured. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Regulatory oversight, including inspections, are carried out during the construction stage in order to ensure that quality assurance -with relevant documentation and records -is applied during construction and that the plant as-built (including authorized modifications), satisfies the design requirements and that other conditions established by the authorization are met. This includes manufacturing activities of items important to safety as well as transportation and storage of such items until erection, to ensure that the characteristics that can only be verified during the manufacturing process are not degraded by subsequent activities. |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. GSR Part 1 (Rev. 1) |  | 51 | Requirement 27, 28, 29 |
| Safety Standards Series No. GSG-13 | Functions and Processes of the Regulatory Body for Safety | 47 |  |
| Safety Standards Series No. SSG-38 | Construction for Nuclear Installations | 26 |  |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| T | How is the leadership and culture for safety of authorized parties overseen by the regulatory body in nuclear power plant? [Topic 7.2] | T | T |
| Expectation | The regulatory framework and the management system of the regulatory body specifies objective and arrangements, including guidance and procedures, for the oversight of leadership and culture for safety of the operating organization, notably through inspection, and review and assessment activities. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Safety is the result of interaction of Human, Technology and Organization (HTO). Therefore, it is critical that regulatory bodies when exercising oversight on the safety of facilities and activities, in conducting their regulatory functions, also cover human and organizational-related factors, including leadership for safety and culture for Safety of the organization. |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. GSR Part 1 (Rev. 1) | Inspection | 52 | 4.53 |
| Safety Standards Series No. GSR Part 2 | Demonstration of leadership for safety by managers | 23 | Requirement 2 |
| Safety Standards Series No. GSR Part 2 | Fostering a culture for safety | 31 | Requirement 12 |
| Safety Standards Series No. GSR Part 2 | Measurement, assessment and improvement of leadership for safety and of safety culture | 33 | Requirement 14 |
| Safety Standards Series No. GSG-13 | Review and Assessment | 85 | 3.200 |
| Safety Standards Series No. GSG-13 | Inspection | 89 | 3.215; 3.220; 3.230 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the regulatory requirements relating to fundamental safety functions, application of defence in depth at NPPs, and categories of plant states. [Topic 9.2] | A | F |
| Expectation | The regulatory framework addresses measures to be taken, including: - Fundamental safety functions (control of reactivity; removal of heat from the reactor and from the fuel store; and confinement of radioactive material, shielding against radiation and control of planned radioactive releases, as well as limitation of accidental radioactive releases); - Application of defence in depth; - Identification and grouping of a limited number of categories of plant states. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The identification of the items important to safety, that are necessary to fulfil the fundamental safety functions, as well as the inherent features that are contributing to fulfilling, or that are affecting the fundamental safety functions for all plant states, are to be subject of a systematic approach. Means of monitoring the status of the plant is to be provided for ensuring that the required safety functions are fulfilled. Application of the concept of defence in depth throughout the design and operation of a NPP provides multilayer protection against a wide range of anticipated operational occurrences, including those resulting from equipment failure or human error within the NPP, as well as from events that originate outside the NPP. The current version of SSR 2/1 includes changes and additions resulting from the outcome of the review of the Fukushima Daiichi NPP accident regarding independence between levels of defence in depth and should be carefully reviewed for applicability. Categories of plant states typically include: - Normal operation; - Anticipated operational occurrences; - Design basis accidents; - Design extension conditions. |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 36 | Requirement 4, 7, 13 Para 2.12-2.14, 4.1-4.2, 4.9-4.13A, 5.1-5.2 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the regulatory requirements for operating organizations of NPPs to establish, implement, assess and continually improve a management system that integrates safety, health and environmental elements to ensure safe operation. [Topic 9.2] | A | F |
| Expectation | The regulatory framework requires operating organizations of NPPs to: - Have the prime responsibility for safety; - Establish, implement, assess and continuously improve an integrated management system that meets the requirements of GSR Part 2; - Establish a structure for the operating organization; - Staff the operating organization with sufficient numbers of competent personnel; - Establish and document the functions, roles and responsibilities of staff; - Establish a formal system for ensuring the continuing safety of the plant design throughout the lifetime of the NPP. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The objective is to ensure that a comprehensive management system is established by the operating organization. The NPP management comprises the members of the operating organization to whom the overall responsibility and the authority for the safety of the NPP have been assigned. It is important that the direction from the regulatory body leads to the establishment of an appropriate management structure and all necessary supporting infrastructures to ensure that the NPP will be designed and operated safely. |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 34 | Requirement 1-3 Para 3.1-3.6 |
| Safety Standards Series No. SSR-2/2 (Rev. 1) |  | 24 | Requirement 1-4, 8, 15 Para 3.1-3.13, 4.25-4.32, 4.52 |

| QTYPE | Primary Question | SA |  | IL |
| --- | --- | --- | --- | --- |
| Boolean | Describe the regulatory requirements for operating organizations of NPPs to monitor and control all activities performed by vendors, contractors and suppliers. [Topic 9.2] | A |  | F |
| Expectation | Vendors, contractors and suppliers are required to either conform to the management system of the operating organization of the NPP or implement their own management system that has been approved by the operating organization of the NPP. In the case where the operating organization is not the design organization, the regulatory framework requires the design organization to establish and implement a management system for ensuring that all relevant safety requirements are met. The operating organization of the NPP has processes and procedures in place for the effective supervision of all activities undertaken by vendors, contractors and suppliers. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |  |
| Help | The objective is to ensure that operating organizations of NPPs maintain control over all activities and do not inadvertently delegate their responsibility for safety. |  |  |  |
| Question Tags (one row per Tag) |  |  |  |  |
| Category | Name |  |  |  |
| References (one row per reference) |  |  |  |  |
| Name | Comments | Page | Para |  |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 34 | Requirement 1-3 Para. 3.1-3.6 |  |
| Safety Standards Series No. SSR-2/2 (Rev. 1) |  | 24 | Requirement 1-3, 8 - Para 3.1-3.9, 4.25-4.32 |  |
| Safety Standards Series No. GSR Part 2 |  | 30 | Req. 11 |  |
| Safety Standards Series No. GS-G-3.1 | Application of the Management System for Facilities and Activities |  |  |  |
| Safety Standards Series No. GS-G-3.5 | The Management System for Nuclear Installations |  |  |  |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the regulatory requirements for NPP operating organizations to verify the safety of their NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework addresses the requirements for: -Safety assessments for licensing purposes; -Periodic safety review; -Audit and review. The regulatory framework specifies that operating organizations of NPPs shall perform systematic safety assessments of their NPPs at regular intervals throughout the plant’s operating lifetime, with due account taken of operating experience and significant new safety related information from all relevant sources, including international standards and operating experience. The regulatory framework specifies that if a subsequent site review indicates that the site is unacceptable and the deficiencies cannot be compensated for by design features, measures for site protection or administrative procedures, the site shall be deemed unsuitable. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The objective is to ensure that the safety of the NPP is adequately reviewed at appropriate intervals to demonstrate that it continues to satisfy an adequate level of safety and will continue to do so for its remaining operational life. The current versions of GSR Part 4 (Rev 1), SSR-2/2 (Rev 1) and SSR-1 include changes and additions resulting from the outcome of the review of the Fukushima Daiichi NPP accident. These changes and additions should be carefully reviewed for applicability. But their consideration should not lead to neglect the other aspects covered by relevant Requirements. Please also refer to safety guides SSG-50 (Operating Experience Feedback for Nuclear Installations), SSG-3 (Development and Application of Level 1 Probabilistic Safety Assessment for Nuclear Power Plants), NS-G-2.13 (Evaluation of Seismic Safety for Existing Nuclear Installations), SSG-4 (Development and Application of Level 2 Probabilistic Safety Assessment for Nuclear Power Plants), SSG-61 (Format and Content of the Safety Analysis Report for Nuclear Power Plants), SSG-2 (Rev 1) (Deterministic Safety Analysis for Nuclear Power Plants) and SSG-25 (Periodic Safety Review for Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. GSR Part 4 (Rev. 1) | Graded approach to safety assessment | 27 | Requirement 1-20 |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 41 | Requirement 10, 42 Para 4.17-4.18, 5.71-5.76 |
| Safety Standards Series No. SSR-1 |  | 24 | Requirement 1-29 |
| Safety Standards Series No. SSR-2/2 (Rev. 1) |  | 134 | Requirement 9, 12, 24 Para 4.33-4.37, 4.44-4.47, 5.27-5.33 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the regulatory requirements for a site evaluation to the extent that is appropriate to the potential hazards presented by NPPs. [Topic 9.2] | A | F |
| Expectation | The requirements for site evaluation for NPPs take account SSR-1 requirements amongst others, in relation to: - Site and regional characteristics; - Natural and human induced external hazards; - Multiple nuclear installations; - Flooding; - Extreme or rare meteorological events; - Fault capability - Ultimate heat sink; - Rare meteorological events such as tornadoes and tropical cyclones; - Geotechnical and geological hazards; - Specific requirements for the characterization of the region under consideration such as use of land and water in the region including dispersion of radioactive material in air and water, and population distribution; - Monitoring of external hazards and site conditions throughout the lifetime of the NPP. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The objective is to ensure that appropriate and comprehensive criteria are specified for the evaluation of the suitability of sites of NPPs and that the results of the evaluation are fully documented. The current version of SSR-1 includes changes and additions resulting from the outcome of the review of the Fukushima Daiichi NPP accident. These changes and additions should be carefully reviewed for applicability, particularly relating to: - The potential occurrence of events in combination; - Establishing levels of hazard for the design basis for the installation and their associated uncertainties; - Multiple facilities at a single site; - Monitoring of hazards and periodic review of site-specific hazards. Please also refer to safety guides SSG-9 (Seismic Hazards in Site Evaluation for Nuclear Installations), NS-G-3.2 (Dispersion of Radioactive Material in Air and Water and Consideration of Population Distribution in Site Evaluation for Nuclear Power Plants), NS-G-2.13 (Evaluation of Seismic Safety for Existing Nuclear Installations), SSG-35 (Site Survey and Site Selection for Nuclear Installations), NS-G-3.6 (Geotechnical Aspects of Site Evaluation and Foundations for Nuclear Power Plants), SSG-79 (Hazards Associated with Human Induced External Events in Site Evaluation for Nuclear Installations), SSG-18 (Meteorological and Hydrological Hazards in Site Evaluation for Nuclear Installations) and SSG-21 (Volcanic Hazards in Site Evaluation for Nuclear Installations). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-1 |  | 24 | Requirement 1-29 |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | Describe the provisions in the regulatory framework relating to consideration of potential combinations of external natural and human induced events in site evaluations. [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The requirements specify that: - Proposed sites for a nuclear installation shall be evaluated with regard to the frequency and severity of external natural and human induced events, and potential combinations of such events, that could affect the safety of the installation; - Information on frequency and severity derived from the characterization of the hazards resulting from external events shall be used in establishing the design basis hazard level for the nuclear installation; - Account shall be taken of uncertainties in the design basis hazard level. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The current version of SSR-1 includes changes and additions resulting from the outcome of the review of the Fukushima Daiichi NPP accident. This subsidiary question aims at addressing changes and additions in the IAEA safety standards resulting from the outcome of the review of the Fukushima Daiichi NPP accident. The consideration of the specific issue should not lead to neglect the other aspects covered by SSR-1 Requirements, basis of the primary question. |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-1 |  | 29 | Requirement 7 Para 4.20, 4.25 |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | Describe the provisions in the regulatory framework relating to consideration of multiple unit NPPs when assessing the feasibility of emergency plans in the frame of site evaluations. [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that an assessment shall be made of the feasibility of implementation of emergency plans. All on-site and co-located installations shall be considered in the assessment, with special emphasis on nuclear installations that could concurrently experience accidents. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The current version of SSR-1 includes changes and additions resulting from the outcome of the review of the Fukushima Daiichi NPP accident. This subsidiary question aims at addressing changes and additions in the IAEA safety standards resulting from the outcome of the review of the Fukushima Daiichi NPP accident. The consideration of the specific issue should not lead to neglect the other aspects covered by SSR-1 Requirements, basis of the primary question. |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-1 |  | 28 | Requirement 5, 13; Para 4.15, 4.42 |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | Describe the requirements regarding seismological data used for assessing the capability of a fault. [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that seismological data used for assessing the capability of a fault shall include palaeoseismological and geomorphological data. |  |  |
| Help | The current version of SSR-1 includes changes and additions resulting from the outcome of the review of the Fukushima Daiichi NPP accident. This subsidiary question aims at addressing changes and additions in the IAEA safety standards resulting from the outcome of the review of the Fukushima Daiichi NPP accident. The consideration of the specific issue should not lead to neglect the other aspects covered by SSR-1 Requirements, basis of the primary question. |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-1 |  | 36 | Requirement 15 Para 5.2 – 5.4 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the regulatory requirements relating to the design of items important to safety for NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework includes requirements about: - Systematic approach to identify items important to safety (Req. 4); - Definition of appropriate characteristics for items important to safety (Req. 6); - Use of relevant national and international codes and standards for the design of items important to safety (Req. 9); - Ensuring that items important to safety can be manufactured, constructed, assembled, installed and erected in such a way that the required safety level will be ensured (Req. 11); - Definition of a design basis for items important to safety (Req. 14); - Definition of design limits for items important to safety (Req. 15); - Design and location to withstand or be protected against the effects of hazards (Para 5.15A under Req. 17); - Application of engineering design rules (Req. 18); - Physical separation and independence of safety systems (Req. 21); - Safety classification of items important to safety and of their support systems (Requirements 22 and 27); - Reliability of items important to safety (Req. 23); - Fail-safe design of systems and components important to safety (Req. 26); - Calibration, testing, maintenance, repair, replacement, inspection and monitoring of items important to safety (Req. 29); - Qualification of items important to safety (Req. 30); - Consideration of ageing phenomena in the design of items important to safety (Req. 31); - Prevention of harmful interaction of systems important to safety (Req. 40); - Functionality of items important to safety not compromised by disturbances in the electrical power grid (Req. 41). Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Please also refer to safety guide SSG-30 (Safety Classification of Structures, Systems and Components in Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 36 | Requirement 4, 6, 9, 11, 14-15, 17-18, 21, 22, -23, 26, 27, 29-31, 40-41 Para 4.1-4.2, 4.5-4.8, 4.14-4.16, 4.19, 5.3-5.4, 5.15A, 5.23, 5.33-5.38, 5.41-5.43, 5.45-5.52, 5.69-5.70 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to the potential for common cause failures and single failure criterion. [Topic 9.2] | A | F |
| Expectation | The regulatory framework includes requirements that the design of equipment is to take due account of the potential for common cause failures of items important to safety, to determine how the concepts of diversity, redundancy, physical separation and functional independence have to be applied to achieve the necessary reliability. (Req. 24) The regulatory framework specifies the single failure criterion to be applied to each safety group incorporated in the plant design (Req. 25). Answer should include a description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help |  |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 51 | Requirement 24, 25 Para 5.39, 5.40 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to safety assessment and safety analysis of NPPs with, in particular, consideration of margins against cliff-edge effects and early or large radiological releases. [Topic 9.2] | A | F |
| Expectation | The regulatory framework specifies that comprehensive deterministic safety assessments and probabilistic safety assessments shall be carried out throughout the design process for a NPP to ensure that all safety requirements on the design of the plant are met throughout all stages of the lifetime of the plant, and to confirm that the design, as delivered, meets requirements for manufacture and for construction, and as built, as operated and as modified. The regulatory framework specifies that “a safety analysis of the design for the NPP shall be conducted in which methods of both deterministic analysis and probabilistic analysis shall be applied to enable the challenges to safety in the various categories of plant states to be evaluated and assessed.” The regulatory framework specifies that “the safety analysis shall provide assurance that uncertainties have been given adequate consideration in the design of the plant and in particular that adequate margins are available to avoid cliff-edge effects and early radioactive releases or large radioactive releases.” Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The difference between safety analysis and safety assessment is commented in the IAEA Safety Glossary. The current versions of SSR-2/1 (Rev 1) and GSR Part 4 (Rev 1) include changes and additions resulting from the outcome of the review of the Fukushima Daiichi NPP accident. These changes and additions should be carefully reviewed. Please refer to safety guides SSG-2 (Deterministic Safety Analysis for Nuclear Power Plants), SSG-3 (Development and Application of Level 1 Probabilistic Safety Assessment for Nuclear Power Plants), SSG-4 (Development and Application of Level 2 Probabilistic Safety Assessment for Nuclear Power Plants), and SSG-61 (Format and Content of the Safety Analysis Report for Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| IAEA Safety Glossary (2007) | Definitions of Analysis and Assessment | 0 |  |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 41 | Requirement 10, 42 Para 4.17-4.18, 5.71-5.76 |
| Safety Standards Series No. GSR Part 4 (Rev. 1) |  | 27 | Requirement 1-20 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements that the design establishes a set of operational limits and conditions for the safe operation of the NPP. [Topic 9.2] | A | F |
| Expectation | The regulatory framework specifies that the following, derived from the design, shall be established: - Safety limits; - Limiting settings for safety systems; - Limits and conditions for normal operation; - Constraints on control systems and procedural constraints; - Requirements for surveillance, maintenance, testing and inspection; - Specified operational configurations; - Action statements. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help |  |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 52 | Requirement 28 Para 5.44 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to the consideration of postulated initiating events for the design of NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework specifies that the design for the NPP shall apply a systematic approach to identifying a comprehensive set of postulated initiating events such that all foreseeable events with the potential for serious consequences and all foreseeable events with a significant frequency of occurrence are anticipated and are considered in the design. The regulatory framework specifies that the list of postulated initiating events shall be justified and used to identify and justify the preventive and protective measures necessary to ensure the required safety functions and to develop the performance requirements for items important to safety. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help |  |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 43 | Requirement 16 Para 5.5-5.15 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to the consideration of design basis accidents for the design of NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework specifies that a set of accidents that are to be considered in the design shall be derived from postulated initiating events for establishing the boundary conditions for the NPP to withstand, without acceptable limits for radiation protection being exceeded. In particular, the regulatory framework specifies that: - Design basis accidents are to be used to define the design bases, including performance criteria, for safety systems and for other items important to safety that are necessary to control design basis accident conditions, with the objective of returning the plant to a safe state and mitigating the consequences of any accidents; - A primary objective shall be to manage design basis accidents so that they have no, or only minor, radiological consequences, on or off the site, and do not necessitate off-site protective actions. The regulatory framework specifies that a set of accidents that are to be considered in the design shall be derived from postulated initiating events for establishing the boundary conditions for the NPP to withstand, without acceptable limits for radiation protection being exceeded. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help |  |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 47 | Requirement 19 Para 5.24-5.26 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to consideration of design extension conditions for the design of NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework specifies that a set of design extension conditions is to be derived on the basis of engineering judgement, deterministic assessments and probabilistic assessments for the purpose of further improving the safety of the NPP by enhancing the plant’s capabilities to withstand, without unacceptable radiological consequences, accidents that are either more severe than design basis accidents or that involve additional failures. These design extension conditions shall be used to identify the additional accident scenarios to be addressed in the design and to plan practicable provisions for the prevention of such accidents or mitigation of their consequences. The regulatory framework specifies that combinations of events and failures including their consequential effects is to be defined and considered in the design. The regulatory framework specifies that each unit of a multiple unit NPP is to have its own safety systems and shall have its own safety features for design extension conditions and that to further enhance safety, means allowing interconnections between units of a multiple unit power plant shall be considered in the design. The regulatory framework includes requirements specifying inter alia that: - The condition that could lead to an early radioactive release or a large radioactive release is ‘practically eliminated’; - Protective actions that are limited in terms of lengths of time and areas of application shall be sufficient for the protection of the public; - Sufficient time shall be available to take such measures. The regulatory framework specifies that combinations of events and failures including their consequential effects shall be defined and considered in the design. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The current version of SSR-2/1 includes changes and additions resulting from the outcome of the review of the Fukushima Daiichi NPP accident. |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 48 | Requirement 20, 33 Para 5.27-5.32, 5.63 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to consideration of internal and external hazards for the design of NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework specifies that all foreseeable internal hazards and external hazards, including the potential for human induced events directly or indirectly to affect the safety of the nuclear power plant, is to be identified and their effects shall be evaluated. Hazards shall be considered in designing the layout of the plant and in determining the postulated initiating events and generated loadings for use in the design of relevant items important to safety for the plant. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Please also refer to safety guides SSG-18 (Meteorological and Hydrological Hazards in Site Evaluation for Nuclear Installations), SSG-64 (Protection against Internal Hazards in the Design of Nuclear Power Plants), SSG-79 (Hazards Associated with Human Induced External Events in Site Evaluation for Nuclear Installations), SSG-18 (Meteorological and Hydrological Hazards in Site Evaluation for Nuclear Installations), SSG-9 (Rev 1) (Seismic Hazards in Site Evaluation for Nuclear Installations), NS-G-3.6 (Geotechnical Aspects of Site Evaluation and Foundations for Nuclear Power Plants), SSG-68 (Design of Nuclear Installations Against External Events Excluding Earthquakes), Replaced by SSG64 mentioned aboveSSG-67 (Seismic Design for Nuclear Installations), SSG-21 (Volcanic Hazards in Site Evaluation for Nuclear Installations) and SSG-35 (Site Survey and Site Selection for Nuclear Installations). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 45 | Requirement 17 Para 5.15A-5.17, 5.19, 5.21, 5.21A |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What are the requirements relating to the specificities of multiple unit plant sites regarding external hazards? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that for multiple unit plant sites, the design shall take due account of the potential for specific hazards to give rise to impacts on several or even all units on the site simultaneously. |  |  |
| Help | The current version of SSR-2/1 includes changes and additions resulting from the outcome of the review of the Fukushima Daiichi NPP accident. This subsidiary question aims at addressing changes and additions in the IAEA safety standards resulting from the outcome of the review of the Fukushima Daiichi NPP accident. The consideration of the specific issue should not lead to neglect the other aspects covered by SSR-2/1 Req. 17, basis of the primary question. |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 45 | Requirement 17 Para 5.15B |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What are the requirements relating to the margin against external hazards? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that the design of the plant shall provide for an adequate margin to protect items important to safety against levels of external hazards to be considered for design, derived from the hazard evaluation for the site, and to avoid cliff edge effects. The regulatory framework specifies that the design of the plant shall also provide for an adequate margin to protect items ultimately necessary to prevent an early radioactive release or a large radioactive release in the event of levels of natural hazards exceeding those considered for design, derived from the hazard evaluation for the site. |  |  |
| Help | The current version of SSR-2/1 includes changes and additions resulting from the outcome of the review of the Fukushima Daiichi NPP accident. This subsidiary question aims at addressing changes and additions in the IAEA safety standards resulting from the outcome of the review of the Fukushima Daiichi NPP accident. The consideration of the specific issue should not lead to neglect the other aspects covered by SSR-2/1 (Rev 1) Req. 17, basis of the primary question. |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 46 | Requirement 17 Para 5.21-5.21A |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to the design of the reactor core and associated features for NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework includes requirements dealing with: - Performance of fuel elements and assemblies regarding their structural integrity under conditions in the reactor core, taking into account all the processes of deterioration that could occur in operational states (Req. 43); - Structural capability of the reactor core, maintaining a geometry under operational states and accident conditions other than severe accidents that allows adequate cooling and insertion of control rods (Req. 44); - Control of the reactor core with a stable neutron distribution in all plant states except severe accident, minimizing the demand on the control system (Req. 45); - Means capable of shutting the reactor down and maintaining shutdown conditions even for the more reactive conditions of the reactor core (Req. 46). Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Please also refer to safety guide SSG-52 (Design of the Reactor Core for Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 61 | Requirement 43-46 Para 6.1-6.12 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to the design of the reactor coolant systems for NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework includes requirements dealing with: - Quality of design and construction (Req. 47); - Overpressure protection to the reactor coolant pressure boundary (Req. 48); - Control of the reactor coolant inventory (Req. 49); - Provision of clean-up facilities to remove radioactive and non-radioactive substances from the reactor coolant (Req. 50); - Provision of residual heat removal means in shutdown states (Req. 51); - Provision of means for emergency cooling of the core capable of restoring and maintaining the cooling of the fuel under accident conditions (Req. 52); - Capability to transfer heat to an ultimate heat sink for all plant states (Req. 53). Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Please also refer to safety guide SSG-56 (Design of the Reactor Coolant System and Associated Systems in Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 64 | Requirement 47-53 Para 6.13-6.19B |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What are the requirements for heat transfer to an ultimate heat sink? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that the capability to transfer heat to an ultimate heat sink shall be ensured for all plant states and that systems for transferring heat shall have adequate reliability for the plant states in which they have to fulfil the heat transfer function, which may require the use of a different ultimate heat sink or different access to the ultimate heat sink. The regulatory framework specifies that the heat transfer function shall be fulfilled for levels of natural hazards more severe than those considered for design, derived from the hazard evaluation for the site. |  |  |
| Help | This subsidiary question aims at addressing changes and additions in the IAEA safety standards resulting from the outcome of the review of the Fukushima Daiichi NPP accident. The consideration of the specific issue should not lead to neglect the other aspects covered by SSR-2/1 (Rev 1) Requirements 47-53, basis of the primary question. Please also refer to safety guide SSG-56 (Design of the Reactor Coolant System and Associated Systems in Nuclear Power Plants). |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 66 | Requirement 53 Para 6.19A-6.19B |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to the containment structure and the containment system for NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework includes requirements dealing with: - Containment system for the reactor (Req. 54); - Control of radioactive releases from the containment in operational states and in accident conditions (Req. 55); - Isolation of the containment (Req. 56); - Access to the containment through airlocks (Req. 57); - Control of containment conditions (Req. 58). Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Please also refer to safety guide SSG-53 (Design of Reactor Containment and Associated Systems for Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 67 | Requirement 54-58; Para 6.20-6.30 |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What are the requirements relating to the prevention of the loss of the structural integrity of the containment? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that design provisions shall be made to prevent the loss of the structural integrity of the containment in all plant states and that the use of this provision shall not lead to an early radioactive release or a large radioactive release. |  |  |
| Help | This subsidiary question aims at addressing changes and additions in the IAEA safety standards resulting from the outcome of the review of the Fukushima Daiichi NPP accident. The consideration of the specific issue should not lead to neglect the other aspects covered by SSR-2/1 (Rev 1) Requirements 54-58, basis of the primary question. |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 69 | Requirement 58 Para 6.28A |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What are the requirements relating to features to restore the capability to remove heat from the containment? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that the design shall include features to enable the safe use of non-permanent equipment for restoring the capability to remove heat from the containment. |  |  |
| Help | This subsidiary question aims at addressing changes and additions in the IAEA safety standards resulting from the outcome of the review of the Fukushima Daiichi NPP accident. The consideration of the specific issue should not lead to neglect the other aspects covered by SSR-2/1 (Rev 1) Requirements 54-58, basis of the primary question. Please also refer to safety guide SSG-53 (Design of Reactor Containment and Associated Systems for Nuclear Power Plants). |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) | Safety of Nuclear Power Plants: Design | 69 | Requirement 58 Para 6.28B |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to the design of instrumentation and control systems for NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework includes requirements relating to: - Provision for instrumentation and the parameters and/or safety functions to be monitored in operational states and in accident conditions (Req. 59); - Provision of control systems to maintain the plant in the specified operating range (Req. 60); - Provision of a protection system capable of detecting unsafe plant conditions and to initiate safety actions automatically to actuate safety systems necessary for achieving and maintaining safe plant conditions (Req. 61); - Reliability and testability of instrumentation and control systems commensurate with the safety functions to be performed (Req. 62); - Application of appropriate standards and practices for the development and testing of computer hardware and software (Req. 63); - Separation of protection systems and control systems (Req. 64); - Provision of a control room from which the plant can be safety operated in all operational states, either automatically or manually, and from which measures can be taken to maintain the plant in a safe state or to bring it back into a safe state after anticipated operational occurrences and accident conditions (Req. 65); - Provision of a supplementary control room separate from the control room from which the plant can be placed and maintained in a safe shutdown state, residual heat can be removed and essential plant variables can be monitored (Req. 66); - Provision of necessary emergency response facilities on the site (Req. 67). Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Req. 32 (design for optimal operator performance) and Req. 37 (communication systems at the plant) in particular shall also be considered for the design of the control room, the supplementary control room and the emergency response facilities on the site. Please also refer to safety guide SSG-39 (Design of Instrumentations and Control Systems for Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 70 | Requirement 59-67 Para 6.31-6.42 |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What are the requirements on design that ensure the protection of control room against the external hazards? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that the design of the control room shall provide an adequate margin against levels of natural hazards more severe than those considered for the design, derived from the hazards evaluation for the site. Furthermore, a protracted period of time shall be specified for the design of the control room to ensure the protection of occupants of the control room against hazards such as high radiation levels resulting from accident conditions, releases of radioactive materials, fire, or explosive or toxic gases. |  |  |
| Help | This subsidiary question aims at addressing changes and additions in the IAEA safety standards resulting from the outcome of the review of the Fukushima Daiichi NPP accident. The consideration of the specific issue should not lead to neglect the other aspects covered by SSR-2/1 (Rev 1) Req. 59-67, basis of the primary question. Please also refer to safety guide SSG-39 (Design of Instrumentations and Control Systems for Nuclear Power Plants). |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 73 | Requirement 65 Para 6.39, 6.40A |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What are the requirements relating to the design of emergency response facilities on the site? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that the NPP shall include the necessary emergency response facilities on the site. Their design shall be such that personnel will be able to perform expected tasks for managing an emergency under conditions generated by accidents and hazards. Information about important plant parameters and radiological conditions at the NPP and in its immediate surroundings shall be provided to the relevant emergency response facilities. Each facility shall be provided with means of communication with, as appropriate, the control room, the supplementary control room and other important locations at the plant, and with on-site and off-site emergency response organizations. |  |  |
| Help | This subsidiary question aims at addressing changes and additions in the IAEA safety standards resulting from the outcome of the review of the Fukushima Daiichi NPP accident. The consideration of the specific issue should not lead to neglect the other aspects covered by SSR-2/1 (Rev 1) Requirements 59-67, basis of the primary question. Req. 32 (design for optimal operator performance) and Req. 37 (communication systems at the plant) in particular shall also be considered for the design of emergency response facilities. Please also refer to safety guide SSG-39 (Design of Instrumentations and Control Systems for Nuclear Power Plants). |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 74 | Requirement 67; Para 6.42 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to the design of the emergency power supply for NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework specifies that the design of a NPP shall include an emergency power supply capable of supplying the necessary power in anticipated operational occurrences and design basis accidents, in the event of a loss of off-site power and that the design shall include an alternative power source to supply the necessary power in design extension conditions. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Please also refer to safety guide SSG-34 (Design of Electric Power Systems for Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 74 | Requirement 68 Para 6.43-6.45A |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What are the requirements relating to the design of the alternate power source? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that--similar to the emergency power supply--the design specifications for the alternate power source includes the requirements for capability, availability, duration of the required power supply, capacity and continuity. In particular, the regulatory framework specifies that the alternate power source shall be capable of supplying the necessary power to preserve the integrity of the reactor coolant system and to prevent significant damage to the core and to spent fuel in the event of the loss of off-site power combined with failure of the emergency power supply. It shall be independent of and physically separated from the emergency power supply. Its connection time shall be consistent with the depletion of the battery. Equipment that is necessary to mitigate the consequences of melting of the reactor core shall be capable of being supplied either by the emergency power supply or by the alternate power source. |  |  |
| Help | This subsidiary question aims at addressing changes and additions in the IAEA safety standards resulting from the outcome of the review of the Fukushima Daiichi NPP accident. The consideration of the specific issue should not lead to neglect the other aspects covered by SSR-2/1 (Rev 1) Req. 68, basis of the primary question. Please also refer to safety guide SSG-34 (Design of Electric Power Systems for Nuclear Power Plants). |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 74 | Requirement 68 Para 6.43, 6.44A -6.44C |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What are the requirements relating to situations where the alternating current (AC) power sources are lost? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that continuity of power for the monitoring of the key plant parameters and for the completion of short-term actions necessary for safety shall be maintained in the event of loss of the AC (alternating current) power sources. |  |  |
| Help | This subsidiary question aims at addressing changes and additions in the IAEA safety standards resulting from the outcome of the review of the Fukushima Daiichi NPP accident. The consideration of the specific issue should not lead to neglect the other aspects covered by SSR-2/1 (Rev 1) Req. 68, basis of the primary question. Please also refer to safety guide SSG-34 (Design of Electric Power Systems for Nuclear Power Plants). |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 75 | Requirement 68 Para 6.44D |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What are the design requirements relating to the use of non-permanent equipment regarding electrical power supply? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that the design shall include features to enable the safe use of non-permanent equipment to restore the necessary electrical power supply. |  |  |
| Help | This subsidiary question aims at addressing changes and additions in the IAEA safety standards resulting from the outcome of the review of the Fukushima Daiichi NPP accident. The consideration of the specific issue should not lead to neglect the other aspects covered by SSR-2/1 (Rev 1) Req. 68, basis of the primary question. Please also refer to safety guide SSG-34 (Design of Electric Power Systems for Nuclear Power Plants). |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 75 | Requirement 68 Para 6.45A |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to the design and performance of supporting systems and auxiliary systems of NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework specifies that the design of supporting systems and auxiliary systems shall be such as to ensure that the performance of these systems is consistent with the safety significance of the system or component that they serve at the NPP. The regulatory framework includes requirements relating to the design and performance of: - Heat transport systems which have to remove heat from systems and components that are required to function in operational states and in accident conditions (Req. 70) - Process sampling systems and post-accident sampling systems that are needed in a timely manner to determine the concentration of specified radionuclides in process systems or in the environment (Req. 71); - Compressed air systems (Req. 72); - air conditioning systems and ventilation systems that are needed to maintain environmental conditions for systems and components important to safety (Req. 73); - Fire protection systems comprising of detection, extinguishing, fire containment barriers and smoke control systems (Req. 74); - Lighting systems (Req. 75); - Overhead lifting equipment (Req. 76). Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Please also refer to safety guides SSG-64 (Protection against Internal Hazards in the Design of Nuclear Power Plants) and SSG-56 (Design of the Reactor Coolant System and Associated Systems in Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 76 | Requirement 69-76 Para 6.46-6.55 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to the design and performance of steam supply system, feedwater system and turbine generator for NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework specifies that the design of steam supply system, feedwater system and turbine generator for the NPP shall be such as to ensure that the appropriate design limits of the reactor coolant pressure boundary are not exceeded in operational states or in accident conditions. The regulatory framework includes requirements relating to: - Steam isolation valve capability; - Capability of the feedwater system to prevent escalation from anticipated operational occurrences to accident conditions; - Turbine generator over speed and vibration protection; - Measures to minimize effects of turbine generated missiles on items important to safety. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Please also refer to safety guide SSG-56 (Design of the Reactor Coolant System and Associated Systems in Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 79 | Requirement 77 Para 6.56-6.58 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to the design of fuel handling and storage systems for NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework specifies that fuel handling and storage systems shall be provided at the NPP to ensure that the integrity and properties of the fuel are maintained at all times during fuel handling and storage. Requirements apply to fresh and spent fuel. Significant damage to items important to safety during the transfer of fuel or casks shall be prevented. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Please also refer to safety guide SSG-63 (Design of Fuel Handling and Storage Systems for Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 80 | Requirement 80 Para 6.64-6.68A |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What are the requirements relating to the prevention of fuel uncovering for reactors using a water pool system for fuel storage? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that for reactors using a water pool system for fuel storage, the design shall be such as to prevent the uncovering of fuel assemblies in all plant states that are of relevance for the spent fuel pool so that the possibility of conditions arising that could lead to an early radioactive release or a large radioactive release is ‘practically eliminated’ and so as to avoid high radiation fields on the site. The design of the plant: (a) Shall provide the necessary fuel cooling capabilities; (b) Shall provide features to prevent the uncovering of fuel assemblies in the event of a leak or a pipe break; (c) Shall provide a capability to restore the water inventory. The design shall also include features to enable the safe use of non-permanent equipment to ensure sufficient water inventory for the long-term cooling of spent fuel and for providing shielding against radiation. |  |  |
| Help | This subsidiary question aims at addressing changes and additions in the IAEA safety standards resulting from the outcome of the review of the Fukushima Daiichi NPP accident. The consideration of the specific issue should not lead to neglect the other aspects covered by SSR-2/1 (Rev 1) Req. 80, basis of the primary question. |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 82 | Requirement 80 Para 6.68 |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What are the requirements relating to the monitoring and control of parameters representative of the spent fuel pool conditions during operational states or accident conditions? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that the design shall include the following: (a) Means for monitoring and controlling the water temperature for operational states and for accident conditions that are of relevance for the spent fuel pool; (b) Means for monitoring and controlling the water level for operational states and for accident conditions that are of relevance for the spent fuel pool; (c) Means for monitoring and controlling the activity in water and in air for operational states and means for monitoring the activity in water and in air for accident conditions that are of relevance for the spent fuel pool; (d) Means for monitoring and controlling the water chemistry for operational states. |  |  |
| Help | This subsidiary question aims at addressing changes and additions in the IAEA safety standards resulting from the outcome of the review of the Fukushima Daiichi NPP accident. The consideration of the specific issue should not lead to neglect the other aspects covered by SSR-2/1 (Rev 1) Req. 80, basis of the primary question. |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 82 | Requirement 80 Para 6.68A |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to optimal operator performance and human factors for the design and safe operation of NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework specifies that: -Human factors are considered at an early stage in the design and continues throughout the design process and into operation; -Ergonomic principles shall be applied in the design of equipment, including control rooms and panels; -Operators shall be provided with clear displays and audible signals for those parameters that are important to safety; -The design shall minimize the demands on operators in operational states and accident conditions; -The need for appropriate control devices (e.g. interlocks, keys, passwords) to anticipate foreseeable human errors shall be taken into account in the design; -Effective means of communication shall be provided throughout the NPP; -The NPP is provided with a sufficient number of safe escape routes. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help |  |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 55 | Requirement 32, 36, 37 Para 5.53-5.62, 5.64-5.67 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the regulatory requirements relating to radiation protection in design for NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework specifies that the design of a NPP shall ensure that radiation doses to workers at the plant and to members of the public: - Do not exceed the dose limits; - Are kept as low as reasonably achievable in operational states for the entire lifetime of the plant; - Remain below acceptable limits and as low as reasonably achievable in, and following, accident conditions. The regulatory framework includes requirements relating to: - Design for radiation protection; - Design of systems containing fissile or radioactive material; - Radiation monitoring; -treatment of waste and effluents in order to keep discharges below authorized limits and as low as reasonable achievable. The regulatory framework specifies that, for NPPs used for cogeneration of heat or power, the design shall prevent the transport of radionuclides from the NPP to the other units under all conditions, including accident conditions. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The objective is to ensure that the design of the NPP results in exposure of workers and the public to radiation being within regulatory limits and kept as low as reasonably achievable. Please also refer to safety guides NS-G-3.2 (Dispersion of Radioactive Material in Air and Water and Consideration of Population Distribution in Site Evaluation for Nuclear Power Plants), NS-G-1.13 (Radiation Protection Aspects of Design for Nuclear Power Plants) and SSG-27 (Rev 1) (Criticality Safety in the Handling of Fissile Material). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. GSR Part 3 | Planned exposure situations | 59 | 3.1-3.85 |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 37 | Requirement 5, 34, 35, 78, 81-82 Para 4.3-4.4, 6.59, 6.60, 6.69-6.84 |

| QTYPE | Primary Question |  |  | SA | IL |
| --- | --- | --- | --- | --- | --- |
| Boolean | Describe the requirements relating to design features to facilitate radioactive waste management and decommissioning of NPPs. [Topic 9.2] |  |  | A | F |
| Expectation | In addressing the design provisions for the management of radioactive waste, the following shall be considered: - Features for facilitating radioactive waste management and the future decommissioning and dismantling of the plant; - System for treating solid radioactive waste and liquid radioactive waste to keep the amounts and concentrations of radioactive releases below the authorized limits on discharges and as low as reasonably achievable; - Systems for treating liquid and gaseous radioactive effluents to keep their amounts below the authorized limits on discharges and as low as reasonably achievable. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |  |  |
| Help | The objective is to ensure the design of the facility optimizes generation of waste during the life of the facility and that all regulatory requirements for discharges and disposal are satisfied. Please also refer to safety guide SSG-47 (Decommissioning of Nuclear Power Plants, Research Reactors and Other Nuclear Fuel Cycle Facilities). |  |  |  |  |
| Question Tags (one row per Tag) |  |  |  |  |  |
| Category | Name |  |  |  |  |
| References (one row per reference) |  |  |  |  |  |
| Name | Comments | Page | Para |  |  |
| Safety Standards Series No. SSR-2/1 (Rev. 1) |  | 17 | Requirement 12, 78-79 Para 4.20, 6.59-6.63 |  |  |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements for operating organizations at NPPs to establish and implement a commissioning programme. [Topic 9.2] | A | F |
| Expectation | If there is an on-going commissioning process or such a process is expected in the foreseeable future for a NPP, the regulatory framework specifies that the operating organization shall ensure a commissioning programme for the NPP is established and implemented. This programme shall: - Cover the full range of NPP conditions required in the design and the safety case; - Allow the operating organization and the regulatory body to define hold points; - Establish, prior to commencing, prerequisites and necessary validations (procedures, contingencies, etc.); - Be divided into stages at the end of which results will be reviewed prior to continuing, in particular prior to fuel handling operations; - Define processes for addressing deviations, modifications and corrective actions during commissioning; - Define the competences, organization, interfaces, and allocation of tasks and responsibilities; -Ensure the performance criteria are met. The requirements also apply to the restart of a NPP after a lengthy shutdown period. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The objective is to ensure that all items important to safety are systematically commissioned and demonstrate that they provide the required safety functions to the performance standards specified in the design. The importance to safety of a comprehensive well executed commissioning programme for a facility cannot be overstated. Commissioning tests often uncover deficiencies with Items that might otherwise not have been discovered until an SSC is required to respond to a plant upset or accident situation. The current version of SSR-2/2 includes changes and additions resulting from the outcome of the review of the Fukushima Daiichi NPP accident. These changes and additions should be carefully reviewed. Please also refer to safety guide SSG-28 (Commissioning for Nuclear Power Plants) and SSG-12 (Licensing Process for Nuclear Installations). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/2 (Rev. 1) |  | 48 | Requirement 25 Para 6.1-6.15 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to the management of operational safety at NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework includes requirements addressing: - Safety policy (Req. 5); - Operational limits and conditions (Req. 6); - Performance of safety related activities (Req. 8); - Monitoring and review of safety performance (Req. 9); - Control of plant configuration (Req. 10); - Management of plant modifications (Req. 11); - Equipment qualification (Req. 13); - Ageing management (Req. 14); - Reports and records (Req. 15); - Where applicable, programme for long term operation (Req. 16). Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Please also refer to safety guides SSG-48 (Ageing Management and Development of a Programme for Long Term Operation of Nuclear Power Plants), SSG-70 (Operational Limits and Conditions and Operating Procedures for Nuclear Power Plants), SSG-71 (Modification to Nuclear Power Plants), SSG-72 (The Operating Organization for Nuclear Power Plants) and GS-G-3.5 (The Management System for Nuclear Installations). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/2 (Rev. 1) |  | 29 | Requirement 5-6, 8-11, 13-16 Para 4.1-4.15, 4.25-4.43, 4.48-4.54 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements for operating organizations at NPPs to develop and maintain the competence of personnel. [Topic 9.2] | A | F |
| Expectation | The regulatory framework includes requirements for operating organizations to establish minimum qualifications for personnel and to develop and deliver training programmes that: - Are commensurate with the assigned functional responsibilities and authorities; - Use a systematic approach to training; - Include update and refresher training; - Cover all operational states of the NPP; - Address NPP modifications in a timely manner. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The objective is to ensure that only suitably qualified and experienced personnel perform duties which can affect safety. Programmes should be established for senior managers, shift supervisors, operators, radiation protection personnel, maintenance personnel, quality assurance personnel and others working at the NPP whose actions can affect safety. Please also refer to safety guides SSG-75 (Recruitment, Qualification and Training of Personnel for Nuclear Power Plants), SSG-72 (The Operating Organization for Nuclear Power Plants) and SSG-76 (Conduct of Operations at Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/2 (Rev. 1) |  | 28 | Requirement 4, 7 Para 3.10-3.13, 4.16-4.24 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements relating to operational safety programmes to be established and implemented by operating organizations of NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework includes requirements addressing: - Consideration of objectives of nuclear security in safety programmes (Req. 17); - Accident management programmes (Req. 19); - Management of radioactive waste (Req. 21); - Fire safety (Req. 22); - Non-radiation related safety (Req. 23); - Feedback of operating experience (Req. 24). Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Please also refer to safety guides SSG-77 (Protection Against Internal and External Hazards in the Operation of Nuclear Power Plants), SSG-72 (The Operating Organization for Nuclear Power Plants), SSG-40 (Predisposal Management of Radioactive Waste from Nuclear Power Plants and Research Reactors), SSG-50 (Operating Experience Feedback for Nuclear Installations), and SSG-54 (Accident Management Programmes for Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/2 (Rev. 1) |  | 40 | Requirement 17, 19, 21-24 Para 5.1, 5.8-5.9, 5.17-5.33 |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What provisions in the regulatory framework deal with accident management programmes of NPP operating organizations? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory frameworks specifies that the operating organization shall establish, and shall periodically review and as necessary revise, an accident management programme. The regulatory framework specifies that the accident management programme shall include technical and administrative measures to mitigate the consequences of an accident. It shall also include procedures in addition to preparatory measures, guidelines, competent staff, training, periodic tests, exercises and drills, and equipment and contingency measures which shall be located and maintained so as to be functional and readily accessible when needed. The accident management programme also shall, for a multiple unit NPP site, consider concurrent accidents affecting all units, the potential interactions between units and the necessary provisions needed to cope with such concurrent accidents. The possibility of degradation of the regional infrastructure and adverse working conditions shall also be considered. |  |  |
| Help | The current version of SSR 2/2 includes changes and additions resulting from the outcome of the review of the Fukushima Daiichi NPP accident. These changes and additions should be carefully reviewed for applicability. Please also refer to safety guide SSG-54 (Accident Management Programmes for Nuclear Power Plants). |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/2 (Rev. 1) |  | 42 | Requirement 19 Para 5.8-5.9 |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What provisions in the regulatory framework deal with arrangements made by the operating organization to ensure fire safety at the NPP? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that appropriate procedures, equipment and staff are in place for effectively coordinating and cooperating with all firefighting services involved. |  |  |
| Help | The current version of SSR 2/2 includes changes and additions resulting from the outcome of the review of the Fukushima Daiichi NPP accident. These changes and additions should be carefully reviewed for applicability. Please also refer to SSG-77 (Protection Against Internal and External Hazards in the Operation of Nuclear Power Plants). |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/2 (Rev. 1) |  | 46 | Requirement 22 Para 5.24 |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What provisions in the regulatory framework deal with operating experience programmes of NPP operating organizations? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that the operating organization shall establish an operating experience programme to learn from events at the plant and events in the nuclear industry and other industries worldwide. The regulatory framework specifies lessons learned are not only drawn but incorporated for the operating organization's operations, including its emergency arrangements. As well, liaison with support organizations for feedback information on operating experience and advice shall cover design, construction, commissioning and operation of the plant. |  |  |
| Help | The current version of SSR-2/2 includes changes and additions resulting from the outcome of the review of the Fukushima Daiichi NPP accident. These changes and additions should be carefully reviewed with regards to these issues. Please refer to safety guide SSG-50 (Operating Experience Feedback for Nuclear Installations). |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/2 (Rev. 1) |  | 46 | Requirement 24 Para 5.27, 5.32 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the regulatory requirements for NPP operating organizations to establish and implement a radiation protection programme. [Topic 9.2] | A | F |
| Expectation | The regulatory framework addresses the specified requirements for: - Radiation protection programme; - Radiation protection personnel; - Reference levels; - Control of occupational exposures; - Contamination control. All activities involving potential radiation exposure are planned, supervised and monitored. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The objective is to ensure that adequate arrangements are implemented to protect workers against the effects of ionizing radiation. Please also refer to safety guides: GSG-7 (Occupational Radiation Protection), SSG-5 (Safety of Conversion Facilities and Uranium Enrichment Facilities), SSG-7 (Safety of Uranium and Plutonium Mixed Oxide Fuel Fabrication Facilities), SSG-40 (Predisposal Management of Radioactive Waste from Nuclear Power Plants and Research Reactors), GSG-9 (Regulatory Control of Radioactive Discharges to the Environment), SSG-44 (Establishing the Infrastructure for Radiation Safety), SSG-6 (Rev 1) (Safety of Uranium Fuel Fabrication Facilities) and RS-G-1.8 (Environmental and Source Monitoring for Purposes of Radiation Protection). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/2 (Rev. 1) |  | 43 | Requirement 20 Para 5.10-5.16 |
| Safety Standards Series No. GSR Part 3 | Radiation Protection and Safety of Radiation Sources: International Basic Safety Standards | 0 |  |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the requirements for operating organizations at NPPs to establish and implement provisions for emergency preparedness and response. [Topic 9.2] | A | F |
| Expectation | [Note: This primary question is only to reveal any specific information related to review and assessment as it applies to NPPs. DO NOT REPEAT information that has already been provided in the core modules dealing with GSR Part 7.] The regulatory framework specifies that the operating organization shall prepare emergency plans that address: - Maintaining protection and safety; - Mitigating consequences of accidents; - Protection of site personnel and the public; - Coordination of activities with other response organizations; - Timely communication with the public; - Emergency organizational structure; - Testing and validation of plans; - Review and updating of plans; - Training programme; - Facilities, instruments, tools, equipment, documentation and communication systems; - Accident management programme; - Provision of relevant information on safety parameters. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The requirements for the regulatory body's emergency preparedness and response are covered by the core question set dealing with GSR Part 1 and GSR Part 7. The current versions of SSR 2/2 and GSR Part 7 address issues identified during the review of the Fukushima Daiichi NPP accident and should be carefully reviewed for applicability. In particular, specific requirements must be in place for the testing and validation of emergency plans. However, their consideration should not lead to neglect the other aspects covered by relevant Requirements, basis of primary questions. Emergency procedures should be based on the accidents analyzed in the safety analysis report as well as those additionally postulated for the purposes of emergency planning. Please also refer to safety guides GSG-2 (Criteria for Use in Preparedness and Response for a Nuclear or Radiological Emergency) and GS-G-2.1 (Arrangements for Preparedness for a Nuclear or Radiological Emergency). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/2 (Rev. 1) |  | 40 | Requirement 18 Para 5.2-5.7 |
| Safety Standards Series No. GSR Part 7 | Preparedness and Response for a Nuclear or Radiological Emergency | 0 |  |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the regulatory requirements relating to NPP operations. [Topic 9.2] | A | F |
| Expectation | The regulatory framework addresses: - Operating procedures (Req. 26); - Operation control rooms and control equipment (Req. 27); - Material conditions and housekeeping (Req. 28); - Chemistry programme (Req. 29); - Core management and fuel handling (Req. 30). Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | Please also refer to safety guides SSG-13 (Chemistry Programme for Water Cooled Nuclear Power Plants), SSG-76 (Conduct of Operations at Nuclear Power Plants), SSG2-73 (Core Management and Fuel Handling for Nuclear Power Plants) and SSG-70 (Operational Limits and Conditions and Operating Procedures for Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/2 (Rev. 1) | Safety of Nuclear Power Plants: Commissioning and Operation - | 50 | Requirement 26-30 Para 7.1-7.29 |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the regulatory requirements for operating organizations at NPPs to conduct maintenance, calibration, testing, surveillance and inspection activities to ensure that items important to safety are able to function in accordance with the design intent and with safety requirements. [Topic 9.2] | A | F |
| Expectation | The regulatory framework requires that maintenance, calibration, testing, surveillance and inspection be performed: - Using written procedures and work permits; - At frequencies defined by the safety case; - Using equipment and items that are identified and controlled. The regulatory framework requires records of maintenance, calibration, testing, surveillance and inspection be kept and assessed. The regulatory framework requires the maintenance, calibration, testing, surveillance and inspection programmes be reviewed periodically. The regulatory framework requires that the outages are managed by establishing and implementing arrangements to ensure the effective performance, planning and control of work activities. Special attention should be given to subordinate operations such as decontamination, washing and preparation for maintenance. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The objective is to ensure that arrangements for maintenance, calibration, testing, surveillance and inspection demonstrate that items important to safety continue to: - satisfy the intent of the design; - Ensure the continuing safety of the NPP during maintenance; - Ensure the NPP is returned to an authorized configuration on completion. Please also refer to safety guide SSG-74 (Maintenance, Testing, Surveillance and Inspection in Nuclear Power Plants). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/2 (Rev. 1) |  | 56 | Requirement 31-32 Para 8.1-8.24 |

| QTYPE | Subsidiary Question | True/False | Compulsory |
| --- | --- | --- | --- |
| T | What are the provisions in the regulatory framework regarding maintenance and testing of non-permanent equipment to be used for accidents more severe than design basis accidents at NPPs? [Topic 9.2] | T | T |
| QData |  |  |  |
| Expectation | The regulatory framework specifies that the operating organization shall establish maintenance programmes for non-permanent equipment to be used for accidents more severe than design basis accidents, in order to maintain high reliability of this equipment. The operating organization shall carry out periodic training and exercises in handling the equipment and connecting it to the NPP. |  |  |
| Help | The current version of SSR-2/2 includes changes and additions resulting from the outcome of the review of the Fukushima Daiichi NPP accident. These changes and additions should be carefully reviewed with regards to these issues. However, their consideration should not lead to neglect the other aspects covered by relevant Requirements, basis of primary questions. |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/2 (Rev. 1) |  | 58 | Requirement 31 Para 8.14A |

| QTYPE | Primary Question | SA | IL |
| --- | --- | --- | --- |
| Boolean | Describe the regulatory requirements relating to the preparation for decommissioning at NPPs. [Topic 9.2] | A | F |
| Expectation | The regulatory framework includes requirements addressing: - Preparation and maintenance of a decommissioning plan; - Funding arrangements; -approval by regulatory body; - Storage, treatment, transport and disposal of waste; - Retaining the appropriate resources expertise and knowledge; - Records and documentation; -review and updating of the plan. Answer should include description of any measures planned to improve compliance with IAEA safety requirements relevant to this area. |  |  |
| Help | The objective is to ensure that adequate arrangements are in place for the safe decommissioning of NPPs. The plan should show that decommissioning can be accomplished safely to meet the defined end state. Please also refer to safety guides SSG-12 (Licensing Process for Nuclear Installations), WS-G-5.2 (Safety Assessment for the Decommissioning of Facilities Using Radioactive Material) and SSG-47 (Decommissioning of Nuclear Power Plants, Research Reactors and Other Nuclear Fuel Cycle Facilities). |  |  |
| Question Tags (one row per Tag) |  |  |  |
| Category | Name |  |  |
| References (one row per reference) |  |  |  |
| Name | Comments | Page | Para |
| Safety Standards Series No. SSR-2/2 (Rev. 1) |  | 60 | Requirement 33 Para 9.1-9.6 |
| Safety Standards Series No. GSR Part 6 | Decommissioning of Facilities | 0 |  |